| Permit requested by: |  |  |  | Date: |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Location of Construction/Renovation: |  |  |  | Project Start Date: |  |  |
| Project Manager/Coordinator: |  |  |  | Estimated Duration: |  |  |
| Capital/Facilities Project: |  |  |  | Project/Facilities Mgr Number: |  |  |
| YES |  | # CONSTRUCTION ACTIVITY |  | YES |  | # INFECTION CONTROL RISK GROUP |
|  |  | Type A: Inspection, non-invasive activity |  |  |  | Group 1: Low Risk |
|  |  | Type B: Small scale, short duration, and minimal dust generating activities |  |  |  | Group 2: Medium Risk |
|  |  | Type C: Activity generates moderate-high levels of dust, requires more than one work shift to complete |  |  |  | Group 3: Medium/High Risk |
|  |  | Type D: Activity generating high levels of dust, major demolition and construction activities requiring consecutive work shifts to complete |  |  |  | Group 4: Highest Risk |
| ## CLASS ## I |  | Date: | ### Dust Control • Immediately replace tiles displaced for visual inspection • Vacuum work area is there is visible dust Plumbing Activities • Schedule water interruptions during low activity (e.g. evenings if at all possible) • Flush water lines prior to reuse • Observe for discolored water • Ensure water temperature meets the standards set by the health care facility • Maintain as dry an environment as possible and report any water leaks that occur to walls and substructures |  |  |  |
|  |  | Initial: |  |  |  |  |
| ## CLASS II |  | Date: | #### Dust Control #### • Wet mop and/or vacuum with HEPA filtered vacuum as necessary • Use drop sheets to control dust • Water mist work surfaces while cutting • Seal windows and unused doors with duct tape • Seal air vents in construction/renovation area • Place dust mat at entrance to and exit from work areas ##### Ventilation • Disable the ventilation system in the construction/renovation area until the project is complete- • Monitor need to change and/or clean filters in construction or renovation area ##### Debris Removal & Cleanup • Contain debris in covered containers or cover with a moistened sheet before transporting for disposal ##### Plumbing Activities • Schedule water interruptions during low activity (e.g. evenings if at all possible) • Flush water lines prior to reuse • Observe for discolored water • Ensure water temperature meets the standards set by the health care facility • Maintain as dry an environment as possible and report any water leaks that occur to walls and substructures |  |  |  |
|  |  | Initial: |  |  |  |  |
| ## CLASS III |  | Date: | ###### Dust Control • Erect an impermeable dust barrier from true ceiling (includes area above false ceilings) to the floor consisting of 2 layers of 6 mil fire-retardant polyethylene and gypsum wallboard protection approved by the multidisciplinary team. •Ensure that negative air units are functioning properly and that the HEPA filters are changed regularly –provide documentation • Ensure that windows, doors, plumbing penetrations, electrical outlets and intake and exhaust vents are properly sealed with plastic and duct taped within the construction/renovation area • Vacuum air ducts and spaces above ceilings if necessary • Do not remove dust barrier until the project is complete and the area has been cleaned thoroughly and inspected • Remove dust barrier carefully to minimize spreading dust and other debris particles associated with the construction project ###### Ventilation • Maintain negative pressure within construction zone by using portable HEPA equipped air filtration units • Ensure air is exhausted directly outside and away from intake vents or filtered through a HEPA filter before being re-circulated • Ensure ventilation system is functioning properly and is cleaned if contaminated by soil or dust after construction or renovation project is complete ###### Debris Removal & Cleanup • Remove debris at the end of the work day whenever possible • Vacuum work area with HEPA filtered vacuums daily or more frequently if needed • Contain debris in covered containers or cover with a moistened sheet before transporting for disposal ###### Plumbing Activities • Flush water lines at construction or renovation site and adjacent patient care areas before patients are readmitted • Schedule water interruptions during low activity (e.g. evenings if at all possible) • Flush water lines prior to reuse; observe for discoloured water • Ensure water temperature meets the standards set by the health care facility • Maintain as dry an environment as possible and report any water leaks that occur to walls and substructures |  |  |  |

| CLASS IV | Date: | Dust Control • Before starting the construction project erect an impermeable dust barrier that also has an anteroom • Place a walk-off mat outside the anteroom in patient care areas and inside the anteroom to trap dust from the workers’ shoes, equipment and debris that leaves the construction zone • Ensure that construction workers leave the construction zone through the anteroom so they can be vacuumed with a HEPA filtered vacuum cleaner before leaving the work site; or that they wear cloth or paper coveralls that are removed each time they leave the work site • Direct all personnel entering the construction zone to wear shoe covers • Ensure that construction workers change the shoe covers each time they leave the work site • Repair holes in walls within 8 hours or seal them temporarily • Wet mop with hospital grade disinfectant • Do not remove dust barrier until the project is complete and the area has been cleaned thoroughly and inspected • Remove dust barrier carefully to minimize spreading dust and other debris particles associated with the construction project • Ensure that windows, doors, plumbing penetrations, electrical outlets and intake and exhaust vents are properly sealed with plastic and duct taped within the construction/renovation area • Vacuum air ducts and spaces above ceilings if necessary Ventilation • Ensure negative pressure is maintained within the anteroom and construction zone • Ensure that negative air units are functioning properly and that the HEPA filters are changed regularly –provide documentation • Ensure ventilation systems are working properly in adjacent areas • Review ventilation system requirements in the construction area with ICP to ensure system is appropriate and is functioning properly ###### Debris Removal & Cleanup • Remove debris at the end of the work day • Vacuum work area with HEPA filtered vacuums daily or more frequently if needed • Contain debris in covered containers or cover with a moistened sheet before transporting for disposal Evaluation • Review infection control measures with other members of the planning team or delegate to evaluate their effectiveness and identify problems at the end of the construction project ###### Plumbing Activities • Flush water lines at construction or renovation site and adjacent patient care areas before patients are readmitted • Schedule water interruptions during low activity (e.g. evenings if at all possible) • Flush water lines prior to reuse • Observe for discoloured water • Ensure water temperature meets the standards set by the health care facility • Maintain as dry an environment as possible and report any water leaks that occur to walls and substructures |  |
| --- | --- | --- | --- |
|  | Initial: |  |  |
| Scope of Work To be Done – (This area is to be filled in by the Contractor) |  |  |  |
| Additional Requirements (This area is to be filled in by infection Control) |  |  |  |
| Permit Issued by: Project Manager/Coordinator or Facilities Manager Date: |  |  | Permit Approved by: Manager/Delegate, Infection Prevention and Control Date: |